J40	FLEXIBLE SHEET TANKING / DAMP PROOFING

To be read with Preliminaries / General conditions.

TYPES  OF TANKING / DAMP  PROOFING

140AJ40/2862	LOOSE LAID POLYEHTYLENE GAS RETARDANT DAMP PROOFING / TANKING

- Substrate : ……………..

-	Manufacturer : RIW Ltd, 487/488 Ipswich Road, Slough, Berkshire SL1 4EQ

Tel : +44 1753 944200

E-mail : technical@riw.co.uk

Web : www.riw.co.uk

- 		Product reference : RIW Structureseal GPT

- Thickness / Gauge : 1.5mm

- Colour : Grey

- Joints :

-	Surfaces to be joined : Clean and dry beyond full width of joint.

- 	Laps (minimum) : 100mm selvedge.

-	Jointing : One continuous strip of RIW Gas Seal Tape HC in lap, over selvedge strip  or  butt jointed over a 300mm wide roll of RIW Sheetseal GR, extending 150mm below adjacent rolls.

- 	Sealing : Roll to provide gas tight joints.

WORKMANSHIP

J40/310	WORKMANSHIP GENERALLY

- Condition of substrate :

-	Clean and even textured, free from voids and sharp protrusions.

-	Moisture content : Compatible with damp proofing / tanking.

- Air and surface temperature : Do not apply sheets if below minimum recommended by sheet manufacturer.

- Condition of membrane at completion :

-	Neat, smooth and fully supported, dressed well into abutments and around intrusions.

-	Completely impervious and continuous.

-	Undamaged. Prevent puncturing during following work.

- Permanent overlying construction : Cover membrane as soon as possible.

J40/320	INSPECTION

- Give notice : Before covering any part of membrane with overlying construction

J40/380	PROTECTION BOARDS FOR DAMP PROOFING / TANKING

-	Manufacturer : RIW Ltd, 487/488 Ipswich Road, Slough, Berkshire SL1 4EQ

Tel : +44 1753 944200

E-mail : technical@riw.co.uk

Web : www.riw.co.uk

- 	Product reference : RIW Double Drain

-	Thickness : 8mm.

-	Application :

- 	Membrane surface : Clean and free from contaminants.

- 	Bonding : RIW Adhesive Tape

- 	Board joints : Overlap

- 	Board contact with membrane : Secure and continuous.

- 	Backfilling : ……….

or

J40/380	PROTECTION BOARDS FOR DAMP PROOFING / TANKING

-	Manufacturer : RIW Ltd, 487/488 Ipswich Road, Slough, Berkshire SL1 4EQ

Tel : +44 1753 944200

E-mail : technical@riw.co.uk

Web : www.riw.co.uk

-	Product reference : RIW Protection Board.

-	Thickness : 3mm.

-	Application :

- 	Membrane surface : Clean and free from contaminants.

- 	Bonding : RIW Adhesive Tape

- 	Board joints : Butted together.

- 	Board contact with membrane : Secure and continuous.

- 	Backfilling : ………..