J40	FLEXIBLE SHEET TANKING / DAMP PROOFING

To be read with Preliminaries / General conditions.

TYPES OF TANKING / DAMP PROOFING

J40/190 	SELF - ADHESIVE BITUMEN DAMP PROOFING / TANKING

- Substrate : …………………

-	Primer : Required to vertical or inclined surfaces - As Clause 335.

-	Manufacturer : RIW Ltd, 487/488 Ipswich Road, Slough, Berkshire SL1 4EQ

Tel : +44 1753 944200

E-mail : technical@riw.co.uk

Web : www.riw.co.uk

-	Product reference : RIW Sheetseal 226.

- Number of layers : One.

- Thickness / Gauge : 1.5mm ( applied )

- Bonding : Full. Smooth out to exclude air.

- Joints :

-	Surfaces to be joined : Clean and dry beyond full width of joint.

-	Laps ( minimum ) : 50mm, side and 100mm end / cut rolls.

-	Sealing : Roll to fully adhere.

- Accessories : Not required.

WORKMANSHIP

J40/310	WORKMANSHIP GENERALLY

- Condition of substrate :

-	Clean and even textured, free from voids and sharp protrusions.

-	Moisture content : Compatible with damp proofing / tanking.

- Air and surface temperature : Do not apply sheets if below minimum recommended by sheet manufacturer.

- Condition of membrane at completion :

-	Neat, smooth and fully supported, dressed well into abutments and around intrusions.

-	Completely impervious and continuous.

-	Undamaged. Prevent puncturing during following work.

- Permanent overlying construction : Cover membrane as soon as possible.

J40/320	INSPECTION

- Give notice : Before covering any part of membrane with overlying construction.

J40/335	PRIMERS

-	Manufacturer : RIW Ltd, 487/488 Ipswich Road, Slough, Berkshire SL1 4EQ

Tel : +44 1753 944200

E-mail : technical@riw.co.uk

Web : www.riw.co.uk

-	Product reference : RIW Sheetseal Primer.

- Coverage per coat ( minimum ) : 8m² / litre.

- Curing : Allow to dry thoroughly before covering.

J40/350A	ANGLES IN BONDED DAMP PROOF MEMBRANE / TANKING

- Fit internal angles with a sand / cement fillet, not less than 40 x 40 mm, unless noted otherwise.

- Reinforcing strip to all angles :

-	Material : As damp proofing / tanking.

-	Width ( minimum ) : 300 mm.

-	Timing : Apply before main sheeting.

- Dressing of main sheeting onto adjacent surfaces (minimum) : 100 mm.

J40/360	JUNCTIONS WITH PROJECTING DPC’S / CAVITY TRAYS

- Adjoining surfaces : Clean and dry.

- DPC’s / cavity trays : Lap and fully bond / seal with sheeting.

-	Laps ( minimum ) : 75mm.

-	Bonding / Sealing : RIW Sheetseal 226 x 150mm wide.

J40/370A	PIPES, DUCTS, CABLES, ETC

- Where these pass through sheeting, make junctions completely impervious using RIW Sheetseal 226 in accordance with the data sheet for the product.

J40/380	PROTECTION BOARDS FOR DAMP PROOFING / TANKING

-	Manufacturer : RIW Ltd, 487/488 Ipswich Road, Slough, Berkshire SL1 4EQ

Tel : +44 1753 944200

E-mail : technical@riw.co.uk

Web : www.riw.co.uk

-	Product reference : RIW Protection Board.

- Thickness : 3mm.

- Application : Membrane surface clean and free from contaminants.

-	Bonding : RIW Adhesive Tape

-	Board joints : Butted together.

-	Board contact with membrane : Secure, full and continuous.

- Backfilling :

or

- See Clause 295.